## Slide 1
Tolerance-Based
Time-Current Coordination

## Slide 2
Fuse coordination uses min & max TCC responses, ensuring curves don’t touch for an appropriate level of current
So why not use this method when coordinating relays?

## Slide 3
12,000
Conventional coordination uses single, nominal TCC lines
0.3 Sec.
CTI
TCC lines are separated by a Coordinating Time Interval (CTI)

## Slide 4
12,000
Current & time tolerances are applied to single, nominal TCCs
Interrupter fault-clear = 0.05 sec. (3~ at 60 Hz)
0.3 Sec.
CTI
C class or 10P20 CT modeled as +/-5% measurement error

## Slide 5
12,000
Resulting time-interval between max & min TCC responses
0.16 Sec.

## Slide 6
12,000
Due to “CTI-slop” we can squeeze in one more device!
0.3 Sec.
CTI

## Slide 7
12,000
Current & time responses modeled as +/-2% tolerance
Interrupter fault-clear = 0.033 sec. (2~ at 60 Hz)
Current response-tolerances include primary-current sensing-device error
0.3 Sec.
CTI

## Slide 8
12,000
Tighter tolerances = More series fault-interrupters
0.3 Sec.
CTI

## Slide 9
12,000
Tolerances are so tight, we can insert yet another device!!
0.3 Sec.
CTI

## Slide 10
12,000
We used TCC tolerance-response bands and coordinated more series devices within the same CTI time-value
12,000
0.3 Sec.
CTI
Good Tolerances / 3-Devices
Better Tolerances / 5-Devices
12,000
(CTI coordinated 2-devices)
CTI / 2-devices
We used the CTI method and coordinated 2-devices

## Slide 11
Whether to use +/-5% or +0/-10% CT error (C class or 10P20)
+0% CT error
-10% CT error
Nominal TCC
Nominal TCC
+5% CT error
-5% CT error
Note: Both TCC bands have the same time and (other) current tolerances (+/-).
C class or 10P20 CTs shall (essentially) not produce more than 10% error from 1-20X rated current.

## Slide 12
+/-5% CT error results in more conservative coordination
+0% CT error
-10% CT error
Nominal TCC
Nominal TCC
+5% CT error
-5% CT error